CHECKING & SETTING APPLIANCE 
BURNER PRESSURES & GAS RATES

General:

Natural gas and Liquefied Petroleum Gas (LPG) should be supplied to appliance burners at the pressure specified by the appliance manufacturer to ensure that expected heat output and efficiency is achieved.

Gas operatives should therefore be capable of carrying out tests to verify correct working pressures and gas volume usage. Gas operatives should also be able to adjust burner pressures when necessary.

This is an essential safety requirement legislated for in the Gas Safety (Installation and Use) regulations.

Due to the many existing appliances in circulation, gas operatives should also be capable of converting and adjusting gas pressures in millibars (mbar) and inches water gauge (ins w.g.). Gas operatives should also be able to convert the gas rate to kilowatts (kW) and British Thermal Units (Btu).

Gas Rate:

General

Undertaking gas burner pressure tests and gas volume measurements (rating) are important aspects of commissioning and fault finding.

Natural gas supplied to an appliance at 20mbar can be reduced via pressure regulations in the appliance to provide a range of pressures at the burner, allowing flexible heat input. LPG appliances are normally limited to a burner pressure of approximately 37mbar for Propane and 28mbar for Butane.

Note: In the case of LPG installations the pipe work should be of sufficient size to prevent a pressure drop greater than 2.5mbar between the final pressure regulator to the property and all appliances when the installation is subject to the anticipated maximum load.

The gas-rating test determines the volume (amount) of gas being burned by an appliance. The test converts the time it takes to pass a known volume of gas through a gas meter to an appliance into the heat input. This figure can then be compared to the appliance’s data plate.

The calorific value (CV) of the gas should also be known to use as a constant figure in the calculation. Gas operatives can carry out this test in a matter of minutes with the use of a stopwatch and a calculator or a pre-calculated gas rate chart.

Burner pressure alone is not positive confirmation that the correct volume of gas is being burned. During commissioning or servicing, a burner would have been “set up” in accordance with the manufacturer’s data plate or written instructions. However, whilst a wrongly sized or blocked injector is unlikely to change the gas pressure at the burner, it could significantly affect the rated heat input and output of the appliance.

The average CVs are:

Natural gas	38.76 M1/m3 (gross)

1040 btu/ft3

Propane gas	93.1MJ/m3 (gross)

2496 btu/ft3

Butane gas	121.8 MJ/m3 (gross)

3265 btu/ft3

Gross and net CVs:

Historically, the heat input of a gas appliance in the UK was given in terms of gross calorific value (CV).

The changeover from gross CV to net CV was undertaken to mirror the ‘Europeanisation’ of appliance safety standards.

The CV of a fuel is, in simple terms, the amount of heat contained in a given amount of that fuel. When fuels that contain hydrogen in their chemical make-up are burned, that hydrogen is converted into water vapor. The water vapor holds some of the heat produced as “latent heat” (in the case of Natural gas, this is about 10% of the total heat). This latent heat is included in the figure given for the gross CV of a fuel, but it is excluded from the figure given for a net CV.

It is therefore important to know, whether the heat input of the appliance is quoted in gross or net CV terms, when carrying out a gas rate check on an appliance.

A gas rate check carried out using a gas meter will normally give you a reading in gross terms. It may then be necessary to convert this reading to net terms depending on the information supplied by the appliance manufacturer.

The ratio of gross to net CV heat input is dependent on the fuel type and is approximately as follows.

Natural gas	1.11:1

Propane	1.09:1

Butane	1.08:1

Therefore, the following calculation would need to be applied.

Example 1:

An open flued appliance with a gross CV input of 27kW using Natural gas would have a net CV heat input of 24.32kW, based on the following calculation.

27 divide 1.11 = 24.32kW (net).

Example 2:

An open-flued appliance with a gross CV heat input of 27kW using Propane gas would have a net CV heat input of 24.77kW, based on the following calculation.

27 divide 1.09 = 24.72kW (net).

Example 3:

An open-flued appliance with a gross CV heat input of 27kW using Butane gas would have a net CV heat input of 25.00kW based on the following calculation.

27 divide 1.08 = 25.00kW (net).

Gas meter types:

The most common domestic gas meter in present use is the ‘U6’ (unit construction) diaphragm type, which measures gas in cubic feet (ft3). However, these are now being replaced by either the ‘G4’, which is a diaphragm meter like the U6 or the next generation ‘E6’ (electronic) meter, which has a smaller case size, equivalent volume and gives a more accurate reading than the ‘U6’ type. Both the G4 and E6 meters measure gas in cubic metres (m3).

Rating Procedure:

Method - cubic feet (ft3): U6 diaphragm meter

a)	Make sure that all other gas appliances are turned off.

b)	Operate the gas appliance that is under check, allowing sufficient time for it to warm 	up (normally 10 minutes), and making sure that it will continue to run throughout the 		check period, e.g. check that any thermostat/controls are set accordingly.

c)	Observe the meter index test dial and record the time (in seconds) taken to pass 		one ft3 of gas. this is normally one complete revolution of the test dial (see figure 		60). Turn off the appliance.

Note: The use of a stopwatch is recommended to be as accurate as possible.

d)	At this point you will need to determine whether the appliance heat input rating is 		expressed in gross or net CV terms.

e)	Table 18 will provide a direct reading for both kW (gross) and kW (net) based on 		the time taken for the meter to pass one cubic foot of Natural gas.

f)	If the gas rate is not to the manufacturer’s requirements, calculate the appliance heat 	input using the formula as follows. If the heat input is still not to the manufacturer’s it 	will be necessary to carry out further checks on the appliance and the installation 		pipe work to establish the cause. Any faults should then be rectified.

The formula is as follows.

seconds in one hour x the CV of the gas

________________________________

one revolution of test dial in seconds

Example A:

A gas operative is to check the heat input of a central heating boiler using Natural gas. The boiler’s data plate reveals a maximum heat input of rating of 15.24kW (gross). The time for one complete revolution of the test dial (1ft3) is 72 seconds, this transposes into the following calculations.

Table 18. Gas rating chart for imperial gas meters (up to 212ft3/hr)

which measure Natural gas, (Average CV = 38.76MJ/m3 -  1040btu ft3

Time (in                                                              Time (in

seconds) to      Heat input      Heat input      seconds) to     Heat input     Heat input

burn 1ft3              in                       in                burn 1ft3              in                     in

at the            kW (gross)       kW (net)            at the            kW (gross)      kW (net)

appliance                                                          appliance

17	64.57	58.17	68	16.14	14.54

18	60.98	54.94	70	15.68	14.13

19	57.77	52.05	74	14.83	13.36

20	54.89	49.45	78	14.07	12.68

21	52.27	47.09	82	13.39	12.06

22	49.90	44.95	86	12.76	11.50

23	47.73	43.00	90	12.20	10.99

24	45.74	41.21	94	11.68	10.52

25	43.91	39.56	98	11.20	10.09

26	42.22	38.04	102	10.76	9.70

27	40.66	36.63	106	10.36	9.33

28	39.20	35.32	110	9.98	8.99

29	37.85	34.30	114	9.63	8.67

30	36.59	32.96	120	9.15	8.24

31	35.41	31.90	130	8.44	7.61

32	34.30	30.90	140	7.84	7.06

33	33.26	29.97	150	7.32	6.59

34	32.29	29.09	160	6.86	6.18

35	31.36	28.25	170	6.46	5.82

36	30.49	27.47	180	6.10	5.49

37	29.67	26.73	190	5.78	5.20

38	28.89	26.02	200	5.49	4.94

39	28.15	25.36	210	5.23	4.71

40	27.44	24.72	220	4.99	4.50

41	26.77	24.12	230	4.77	4.30

42	26.14	23.55	240	4.57	4.12

43	25.53	23.00	250	4.39	3.96

44	24.95	22.48	260	4.22	3.80

45	24.39	21.98	270	4.07	3.66

46	23.86	21.50	280	3.92	3.53

47	23.36	21.04	290	3.79	3.41

48	22.87	20.60	300	3.66	3.30

49	22.40	20.18	310	3.54	3.19

50	21.95	19.78	320	3.43	3.09

52	21.11	19.02	330	3.33	3.00

54	20.33	18.31	340	3.23	2.91

56	19.60	17.66	350	3.14	2.83

58	18.93	17.05	360	3.05	2.75

60	18.30	16.48	370	2.97	2.67

62	17.70	15.95	380	2.89	2.60

64	17.15	15.45	390	2.81	2.54

66	16.63	14.98	400	2.74	2.47

3600 (no of seconds) x 1040 (CV of gas)

_______________________________

72 (no of seconds)

or

3744000

________   =   52000 btu hr input

72

To then convert btu’s to kW

52000

____________            =    15.24kW (gross)

3412 (btu’s per kW

Note: To convert a gross CV to a net CV, divide the gross figure by 1.11  (Natural gas), 1.09 (Propane), and 1.08 (Butane). See Gross and net CV’s on chart.

Method - cubic metres (m3) Electronic or metric diaphragm meter:

Because E6/G4 meters do not have a test dial (see figure 61). the gas rating test and calculation is different from that of the U6 meter test.

E6/G4 meters measure gas in cubic metres (m3), not cubic feet (ft3). The figures on the meter index display move significantly more quickly than those on the U6 meter and update the gas flow volume should be timed over a two-minute period.

Procedure:

a)	Make sure that all other gas appliances are turned off.

b)	Operate the gas appliance that is under check, allowing sufficient time for it to warm 		up (normally 10 minutes), and making sure that it will continue to run throughout the 		check period, e.g. check that any thermostat/controls are set accordingly.

c)	Record the meter reading.

d)	After 2 minutes, take another reading. Turn off the appliance, and subtract the first 		reading from the second reading.

Note: The use of a stopwatch is recommended to be as accurate as possible.

c)	At this point you will need to determine whether the appliance heat input rating is 		expressed in gross or net CV terms.

d)	Table 19 is a chart showing the amount of gas passed in a 2 minute test period in m3.

e)	If the gas rate is not to the manufacturer’s requirements, calculate the appliance   heat input using the following formula. If the heat input is still not to the manufacturer’s requirements, it will be necessary to carry out further checks on the appliance and the installation to establish the cause. Any faults should then be rectified.

The formula is as follows.

kW  =  a x b x c

______

d

a  = number of seconds in one hour

b  = cubic metres (m3)

c  = number of kW/m3 (NG)*

d  = 120 seconds (plus number of seconds till the next digit appears on the test drum or

electronic display)

Note:  To determine the number of kW in 1m3 of Natural gas, Propane or Butane, divide the

CV of the gas (in MJ/m3) by 3.6. Therefore:

Natural gas  = 10.76

Propane       = 25.86

Butane        = 33.83

Therefore the calculation looks like this:

kW  = 3600 x m3 x 10.76

______________

time in seconds

Example:

*   first reading            = 99999.010m3

*   second reading     = 99999.052m3

difference between the two readings

=  0.042m3

3600 x 0.042 x 10.76       1626.9

________________   =   ______

123                           123

=  13.23kW (gross)

Table 19. Gas rating chart for metric gas meters (up to 6m3/hr) which

measure Natural gas in cubic metres (m3) (Average Calorific Value = 38.76 MJ/m3

2 Min   Heat   Heat   2 Min   Heat   Heat   2 min   Heat   Heat  2 min   Heat   Heat

gas    input  input     gas   input  input     gas    input  input   gas    input  input

flow     kW      kW      flow      kW      kW      flow     kW       kW    flow     kW      kW

m3  (gross)  (net)      m3   (gross)  (net)       m3  (gross)  (net)     m3   (gross)  (net)

0.002	0.65	0.58	0.052	16.80	15.13	0.102	32.95	29.68	0.152	49.10	44.23

0.004	1.29	1.16	0.054	17.44	15.71	0.104	33.59	30.26	0.154	49.74	44.81

0.006	1.94	1.75	0.056	18.09	16.30	0.106	34.24	30.85	0.156	50.39	45.39

0.008	2.58	2.33	0.058	18.73	16.88	0.108	34.88	31.43	0.158	51.03	45.98

0.010	3.23	2.91	0.060	19.38	17.46	0.110	35.53	32.01	0.160	51.68	46.56

0.012	3.85	3.49	0.062	20.03	18.04	0.112	36.18	32.59	0.162	52.33	47.14

0.014	4.52	4.07	0.064	20.67	18.62	0.114	36.82	33.17	0.164	52.97	47.72

0.016	5.17	4.66	0.066	21.32	19.21	0.116	37.47	33.75	0.166	53.62	48.30

0.018	5.81	5.24	0.068	21.96	19.79	0.118	38.11	34.34	0.168	54.26	48.89

0.020	6.46	5.82	0.070	22.61	20.37	0.120	38.76	34.92	0.170	54.91	49.47

0.022	7.11	6.40	0.072	23.26	20.95	0.122	39.41	35.50	0.172	55.56	50.05

0.024	7.75	6.98	0.074	23.90	21.53	0.124	40.05	36.08	0.174	56.20	50.63

0.026	8.40	7.57	0.076	24.55	22.12	0.126	40.70	36.66	0.176	56.85	51.21

0.028	9.04	8.15	0.078	25.19	22.70	0.128	41.34	37.25	0.178	47.49	51.80

0.030	9.69	8.73	0.080	25.84	23.28	0.130	41.99	37.83	0.180	58.14	52.38

0.032	10.34	9.31	0.082	26.49	23.86	0.132	42.64	38.41	0.182	58.79	52.96

0.034	10.98	9.89	0.084	27.13	24.44	0.134	43.28	38.99	0.184	59.43	53.54

0.036	11.63	10.48	0.086	27.78	25.03	0.136	43.93	39.57	0.186	60.08	54.12

0.038	12.27	11.06	0.088	28.42	25.61	0.138	44.57	40.16	0.188	60.72	54.71

0.040	12.92	11.64	0.090	29.07	26.19	0.140	45.22	40.74	0.190	61.32	55.29

0.042	13.57	12.72	0.092	29.72	26.77	0.142	45.87	41.32	0.192	62.02	55.87

0.044	14.21	12.80	0.094	30.36	27.35	0.144	46.51	41.90	0.194	62.66	56.45

0.046	14.86	13.39	0.096	31.01	27.94	0.146	47.16	42.48	0.196	63.31	57.03

0.048	15.50	13.97	0.098	31.65	28.52	0.148	47.80	43.07	0.198	63.95	57.62

0.050	16.15	41.55	0.100	32.30	29.10	0.150	48.45	43.65	0.200	64.60	58.20